## EN
Appendix C: Design features checklist for new heritage collection facilities This checklist includes all the preventive conservation features that are highly recommended by CCI, as well as those that are specifically required by the Designation and Indemnification programs.
● | Features that are highly recommended by CCI.
♦ | Features that are required by the Designation of Institutions and Public Authorities Program (Designation) or the Canada Travelling Exhibitions Indemnification Program (Indemnification).
▲ | If these features are not present, assessors for the Designation or Indemnification programs are likely to require further clarification. Please contact CCI to discuss your specific case.
(blank) | Features not directly assessed by facility evaluation forms or specific to the Designation or Indemnification programs; assessors may require further clarification.
Date modified: March 19, 2025. This version supersedes any previously published or circulated versions. To ensure you are consulting the latest version, please visit the CCI website.
No. | Features | Recommended by CCI | Required |  | Design feature is included √ | Comments
|  |  | Category A Designation | Indemnification
1. Building
Architectural
A1.01 | The building is not located in a flood-prone area. | ● | ▲ | ▲
A1.02 | The building is located in a flood-prone area, but all rooms that could contain collections are situated above the anticipated flood level. | ● | ▲ | ▲
A1.03 | The building is not located in an industrial area or near other activities exposing the collection to fire, theft, water, pollutants, pests or vibrations and shocks. | ● | ▲ | ▲
A1.04 | The site is graded to provide drainage away from the building. | ● | ▲ | ▲
A1.05 | The institution does not share its building with occupants that are unprotected against fire. | ● | ▲ | ▲
A1.06 | There are clear sightlines to all entrances. | ● | ▲ | ▲
A1.07 | Non-emergency exterior doors have deadbolt locks. | ● | ▲ | ▲
A1.08 | Hinges for exterior doors are designed so that pins cannot be removed. | ● | ▲ | ♦
A1.09 | Exterior doors have high performance, pest-proof seals. | ●
A1.10 | The building is fire resistive or non-combustible. | ● | ▲ | ♦
A1.11 | Clearance is sufficient to manoeuvre objects safely throughout the building (ceiling heights, door widths, elevator size, turning radius). | ●
A1.12 | The roof is not easily accessible from the exterior. | ● | ▲ | ▲
A1.13 | Ducts or vents are larger than 25 cm × 25 cm (10 in. × 10 in.), are protected by an alarm system and have security screens or bars. | ● | ♦ | ♦
A1.14 | The building has fire walls, barriers, stops and separations. | ● | ♦ | ♦
A1.15 | Penetrations in fire-rated walls and ceilings are sealed with fire-rated materials. | ● | ♦ | ♦
A1.16 | Combustible and flammable liquids are properly stored (for example, in an approved cabinet). | ● | ▲ | ▲
A1.17 | The freight elevator is restricted to staff (that is, it cannot be used by the public or caterers). | ● | ▲ | ▲
A1.18 | Emergency staircases in multi-level buildings are enclosed. | ● | ♦ | ♦
Electrical
E1.01 | Main entrances are lit from the outside. | ● | ▲ | ▲
E1.02 | Exterior lighting systems are vandal-proof. | ● | ▲ | ▲
E1.03 | The intrusion alarm system is monitored 24/7. | ● | ♦ | ♦
E1.04 | Ground-floor windows are protected from intrusion (for example, glass break detection, functioning locks and security bars). | ● | ▲ | ♦
E1.05 | Skylights are equipped with an alarm system or security bars. | ● | ▲ | ▲
E1.06 | There is CCTV camera coverage of the building’s main entrances and exits. | ● | ▲ | ♦
E1.07 | There is CCTV camera coverage of areas where collections are present. | ● | ▲ | ▲
E1.08 | There are door contact sensors on all exterior doors. | ● | ♦ | ♦
E1.09 | There is an uninterrupted power supply for the security alarm system. | ● | ♦ | ♦
E1.10 | A fire alarm system (including smoke or heat detectors) is installed throughout the building. The system must be listed with Underwriters Laboratories of Canada and installed in accordance with approved standards. | ● | ♦ | ♦
E1.11 | The fire alarm system has a dedicated phone line that is supervised to detect breaks, grounds and other faults. | ● | ▲ | ▲
E1.12 | The fire alarm system is monitored 24/7. | ● | ♦ | ♦
E1.13 | The fire alarm system operates on standby power during a power failure. | ● | ♦ | ♦
E1.14 | There is a fire zone annunciator panel. | ● | ♦ | ♦
E1.15 | Any fire doors kept open are equipped with automatic closing devices. | ● | ♦ | ♦
Mechanical
M1.01 | An automatic fire suppression system is installed throughout the building. | ● | ▲ | ▲
M1.02 | The automatic fire suppression system is designed and installed in accordance with applicable standards (for example, NFPA 13). | ● | ♦ | ♦
M1.03 | In the event of a fire, the air circulation system shuts down automatically. | ● | ▲ | ♦
M1.04 | The HVAC system has built-in redundancy. | ●
M1.05 | Overall building pressure relative to the outdoors is appropriate to the local climate. | ●
M1.06 | Final stage air filtration is a minimum MERV 12. | ● | ▲ | ▲
M1.07 | Facilities located in areas with higher pollutant concentrations have corresponding filtration. | ● | ▲ | ▲
2a. Collection storage rooms
Architectural
A2a.01 | Storage rooms are not located in the basement, particularly if the building is in a flood-prone area. | ● | ▲ | ▲
A2a.02 | Climate-controlled areas do not have exterior walls. If this is unavoidable, these walls are insulated and have continuous vapour barriers. | ● | ▲ | ▲
A2a.03 | There are no windows. | ● | ▲ | ▲
A2a.04 | The storage room area has a rectangular floor plan (without rounded or polygonal walls). | ●
A2a.05 | Access doors to climate-controlled areas have high-performance seals. | ●
A2a.06 | There are two sets of doors (vestibule) to separate areas that are climate controlled from those that are not. | ●
A2a.07 | Clearance height is sufficient. | ●
A2a.08 | Selected finishes and coatings for storage rooms are safe for objects. The minimum four days of drying time is respected. | ●
A2a.09 | There is no carpet. | ● | ▲ | ▲
A2a.10 | Exposed concrete surfaces are sealed or painted. | ●
A2a.11 | Walls, ceiling, doors and hardware are fire-rated for at least 60 minutes. | ● | ♦ | ♦
A2a.12 | Fire extinguishers are nearby. | ● | ♦ | ♦
A2a.13 | Any cellulose nitrate film has proper storage. | ● | ♦ | ▲
A2a.14 | A minimum of 10% of the space is available for collection growth. | ● | ▲ | ▲
A2a.15 | Storage rooms do not have overhead flat roofs. | ●
A2a.16 | Storage rooms do not have overhead pipes, washrooms, kitchens, air handlers and mechanical rooms. | ● | ▲ | ▲
A2a.17 | Storage rooms are separated from areas that could contain food or food waste (preparation areas, catering stations, kitchens, garbage rooms). | ● | ♦ | ♦
A2a.18 | Collection objects are stored 10 cm to 15 cm above floor level. | ● | ▲ | ▲
A2a.19 | Solid doors, preferably steel doors, with non-removable hinge pins and deadbolt lock are keyed separately. | ● | ▲ | ▲
Electrical
E2a.01 | Lights can be switched off when the space is unoccupied. | ● | ▲ | ▲
E2a.02 | Light sources emit no or very little UV (no more than 10 µW/lm), which is ensured by using no- or low-UV sources (for example, LEDs or low-UV fluorescent tubes) or anti-UV filters that exclude up to 400 nm. | ● | ▲ | ▲
E2a.03 | Devices that can detect movement (for security purposes) are installed. | ● | ♦ | ♦
E2a.04 | CCTV cameras capture who enters and exits the space. | ● |  | ▲
E2a.05 | There are door contact sensors. | ● | ♦ | ♦
E2a.06 | Storage rooms are equipped with an alarm system that can be activated during public hours. | ●
E2a.07 | There is an electronic card access system (or equivalent). | ●
E2a.08 | Ground-level water detectors are connected to the alarm system for storage rooms that are below grade or exposed to water pipes. | ● | ▲ | ▲
E2a.09 | Ground-level water detectors are connected to the alarm system for storage rooms that are at grade level in the case of slab-on-grade construction. | ●
E2a.10 | There is a separate fire zone on the annunciator panel for storage rooms. | ●
E2a.11 | There are smoke detectors connected to the fire alarm system. | ● | ♦ | ♦
Mechanical
M2a.01 | Climate conditions (temperature and RH) eliminate all major risks to the collection. | ● | ♦ | ♦
M2a.02 | The institution maintains at least ASHRAE B for cultural property classes 1, 2, 3, 4, 5, 6 and 8. |  | ♦ | n/a
M2a.03 | The institution maintains at least ASHRAE B or uses cool, cold or frozen storage for cultural property Class 7 (archival material). |  | ♦ | n/a
M2a.04 | Cultural property Class 9 objects (audiovisual collections) can be placed in cool, cold or frozen storage. |  | ♦ | n/a
M2a.05 | At the very least, the institution meets lenders’ climate control requirements. | ●
M2a.06 | The institution maintains at least ASHRAE A1 or A2. |  |  | ♦
M2a.07 | Final stage air filtration is a minimum MERV 12. | ● | ▲ | ▲
M2a.08 | Facilities located in areas with higher pollutant concentrations have corresponding filtration. | ● | ▲ | ▲
M2a.09 | Ductwork is minimized inside storage rooms. | ●
M2a.10 | RH and temperature sensors are located in all spaces and not only in the return air ducts. | ● | ▲ | ▲
M2a.11 | RH and temperature sensors are not located near open doors, in front of vents, on exterior walls or in full sun. | ●
M2a.12 | Climate readings can be taken at frequent (for example, 20-minute) intervals, and data can be downloaded and archived for later interpretation. | ● | ♦ | ♦
M2a.13 | Floor drains and a sump pump are installed in storage rooms that are below grade or that are exposed to water pipes. The system is also equipped with backflow preventors. | ● | ♦ | ▲
M2a.14 | Floor drains are installed in storage rooms located at grade level for slab-on-grade construction. The system is also equipped with backflow preventers. | ●
M2a.15 | There is automatic fire suppression. | ● | ▲ | ▲
Structural
S2a.01 | Floors can withstand the weight of collection and storage furniture. | ●
S2a.02 | The building is equipped with adequate mechanisms and structural features to guarantee the safety of stored objects. | ●
S2a.03 | Collections are protected against seismic shock in high-risk seismic zones. | ● | ♦ | ♦
2b. Collection support spaces (workshops, collections preparation, quarantine rooms, etc.)
Architectural
A2b.01 | Climate-controlled areas do not have exterior walls. If this is unavoidable, these walls are insulated and have continuous vapour barriers. | ●
A2b.02 | Access doors to climate-controlled areas have high-performance seals. | ●
A2b.03 | There are two sets of doors (vestibule) to separate areas that are climate controlled from those that are not. | ●
A2b.04 | Clearance height is sufficient. | ●
A2b.05 | Selected finishes and coatings for rooms are safe for objects. The minimum four days of drying time is respected. | ●
A2b.06 | There is no carpet. | ●
A2b.07 | Exposed concrete surfaces are sealed or painted. | ●
A2b.08 | Fire extinguishers are located nearby. | ● | ♦
A2b.09 | Collection support spaces do not have overhead pipes, washrooms, kitchens, air handlers and mechanical rooms. | ●
A2b.10 | Workshops where dust is produced are well sealed and equipped with local extraction or filtration. | ●
A2b.11 | All spaces where collection objects could be present are separated from areas that could contain food or food waste (preparation areas, catering stations, kitchens, garbage rooms). | ● | ♦ | ♦
Electrical
E2b.01 | Lights can be switched off when the space is unoccupied. | ●
E2b.02 | Light sources emit no or very little UV (no more than 10 µW/lm), which is ensured by using no- or low-UV sources (for example, LEDs or low-UV fluorescent tubes) or anti-UV filters that exclude up to 400 nm. | ●
E2b.04 | Devices that can detect movement (for security purposes) are installed. | ●
E2b.05 | CCTV cameras are installed. | ●
E2b.06 | There are contact sensors on doors and operable windows. | ●
E2b.07 | Rooms that are below grade or that are exposed to water pipes are equipped with ground-level water detectors that are connected to the alarm system. | ●
E2b.08 | The facility has smoke detectors connected to the fire alarm system. | ●
Mechanical
M2b.01 | Final stage air filtration is a minimum MERV 12. | ●
M2b.02 | Facilities located in areas with higher pollutant concentrations have corresponding filtration. | ●
M2b.03 | If dealing with large quantities of mouldy materials, there are special features to contain the spread of spores throughout the facility (special filtration, negative pressure, vestibules). | ●
M2b.04 | Workshops operate with negative pressure. | ●
M2b.05 | Conservation laboratories, collection preparation rooms, quarantine rooms or other spaces where staff work with the collection are climate controlled to the same level as storage rooms and exhibition areas. | ● | ▲
M2b.06 | Spaces such as hallways that connect spaces where collection objects could be present are climate controlled to the same level as storage rooms and exhibition areas. | ● | ▲
M2b.07 | RH and temperature sensors are located in all spaces and not only in the return air ducts. | ●
M2b.08 | RH and temperature sensors are not located near windows, open doors, in front of vents, on exterior walls or in full sun. | ●
M2b.09 | Climate readings can be taken at frequent (for example, 20-minute) intervals, and data can be downloaded and archived for later interpretation. | ●
M2b.10 | Floor drains and a sump pump are installed in spaces where collection objects could be present and that are below grade or are exposed to water pipes. The system is also equipped with backflow preventors. | ●
Structural
S2b.01 | Floors can withstand the weight of objects. | ●
S2b.02 | Collections are protected against seismic shock in high-risk seismic zones. | ●
3. Exhibition areas
Architectural
A3.01 | Exhibition areas are not located below the anticipated flood level if the building is located in a flood-prone area. | ● |  | ▲
A3.02 | Climate-controlled areas do not have exterior walls. If this is unavoidable, these walls are insulated and have continuous vapour barriers. | ● | ▲ | ▲
A3.03 | There are no glass walls, large windows or skylights. | ● | ▲ | ▲
A3.04 | Individual exhibition areas or groups of exhibition areas are separated from other spaces by means of doors. | ● | ♦ | ♦
A3.05 | Access doors to climate-controlled areas have high-performance seals. | ●
A3.06 | There are two sets of doors (vestibule) to separate areas that are climate controlled from those that are not. | ●
A3.07 | Clearance height is sufficient. | ●
A3.08 | Rooms: selected finishes and coatings are safe for objects. The minimum four days of drying time is respected. | ● |  | ♦
A3.09 | Display cases: selected finishes and coatings are safe for objects. The minimum drying time of four weeks is respected. | ● |  | ♦
A3.10 | There is no carpet. | ● | ▲ | ▲
A3.11 | Exposed concrete surfaces are sealed or painted. | ●
A3.12 | Individual exhibition areas or groups of exhibition areas are contained in a compartment that can provide at least 60 minutes of fire resistance. | ● | ▲ | ▲
A3.13 | Fire extinguishers are located nearby. | ● | ♦ | ♦
A3.14 | Exhibition areas are separated from areas that could contain food or food waste (preparation areas, catering stations, kitchens, garbage rooms). | ● | ♦ | ♦
A3.15 | Exhibition areas do not have overhead pipes, washrooms, kitchens, air handlers and mechanical rooms. | ●
A3.16 | There is no direct egress from exhibition areas to the outdoors. | ● | ▲ | ▲
Electrical
E3.01 | Light levels as low as 50 lux can be achieved (some lenders require even lower levels for highly light-sensitive objects). | ●
E3.02 | Light sources emit no or very little UV (no more than 10 µW/lm), which is ensured by using no- or low-UV sources (for example, LEDs or low-UV fluorescent tubes) or anti-UV filters that exclude up to 400 nm. | ●
E3.03 | Light sources have a CRI above 90 and an R9 of at least 50 for a good quality light and at least 90 for an excellent quality light. | ●
E3.04 | Devices that can detect movement (for security purposes) are installed. | ● | ♦ | ♦
E3.05 | CCTV cameras are installed. | ● | ▲ | ♦
E3.06 | There are door contact sensors. | ● | ▲ | ▲
E3.07 | There is an electronic card access system (or equivalent). | ●
E3.08 | Emergency exits are protected by an alarm system 24/7, and where direct egress from exhibition areas to the outdoors is unavoidable, delayed egress is provided where permissible under the National Building Code of Canada or other codes. | ● |  | ♦
E3.09 | Smoke detectors are connected to the fire alarm system. | ● | ♦ | ♦
Mechanical
M3.01 | Climate conditions eliminate all major risks to most of the collection. | ● | ♦ | ♦
M3.02 | The institution maintains at least ASHRAE B for cultural property classes 1, 2, 3, 4, 5, 6, 7 and 8. |  | ♦ | n/a
M3.03 | At the very least, the institution meets lenders’ climate control requirements. |  |  | ♦
M3.04 | Final stage air filtration is a minimum MERV 12. | ● | ▲ | ▲
M3.05 | Facilities located in areas with higher pollutant concentrations have corresponding filtration. | ● | ▲ | ▲
M3.06 | HR and temperature sensors are located in all spaces, not only in the return air ducts. | ●
M3.07 | HR and temperature sensors are not located near windows, open doors, in front of vents, on exterior walls or in full sun. | ●
M3.08 | Climate readings can be taken at frequent (for example, 20-minute) intervals, and data can be downloaded and archived for later interpretation. | ● | ♦ | ♦
M3.09 | Each space has independent controls, which can be adjusted based on occupancy loads or lender requirements. | ●
M3.10 | There is automatic fire suppression. | ● | ▲ | ▲
Structural
S3.01 | Floors can withstand the weight of objects on display. | ●
S3.02 | Adequate structural features permit the safe installation of objects on display. | ●
S3.03 | Collections are protected against seismic shock in high-risk seismic zones. | ● | ♦ | ♦
4. Collection reading rooms
Architectural
A4.01 | Climate-controlled areas do not have exterior walls. If this is unavoidable, these walls are insulated and have continuous vapour barriers. | ● | ▲ | n/a
A4.02 | There are no glass walls, large windows or skylights. | ● | ▲ | n/a
A4.03 | Access doors to climate-controlled areas have high-performance seals. | ● |  | n/a
A4.04 | There are two sets of doors (vestibule) to separate areas that are climate controlled from those that are not. | ● |  | n/a
A4.05 | Rooms: selected finishes and coatings are safe for objects. The minimum four days of drying time is respected. | ● |  | n/a
A4.06 | There is no carpet. | ● | ▲ | n/a
A4.07 | Exposed concrete surfaces are sealed or painted. | ● |  | n/a
A4.08 | Reading rooms are contained in a compartment that can provide at least 60 minutes of fire resistance. | ● | ♦ | n/a
A4.09 | Fire extinguishers are located nearby. | ● | ♦ | n/a
A4.10 | Reading room areas are separated from areas that could contain food or food waste (preparation areas, catering stations, kitchens, garbage rooms). | ● | ♦ | n/a
A4.11 | Reading room areas do not have overhead pipes, washrooms, kitchens, air handlers and mechanical rooms. | ● |  | n/a
A4.12 | There is no direct egress from collection reading rooms to the outdoors. | ● | ▲ | n/a
Electrical
E4.01 | Light sources emit no or very little UV (no more than 10 µW/lm), which is ensured by using no- or low-UV sources (for example, LEDs or low-UV fluorescent tubes) or anti-UV filters that exclude up to 400 nm. | ● |  | n/a
E4.02 | Devices that can detect movement (for security purposes) are installed. | ● | ♦ | n/a
E4.03 | CCTV cameras are installed. | ● | ▲ | n/a
E4.04 | There are door contact sensors. | ● | ▲ | n/a
E4.05 | There is an electronic card access system (or equivalent). | ● |  | n/a
E4.06 | Emergency exits are protected by an alarm system 24/7, and where direct egress from exhibition areas to the outdoors is unavoidable, delayed egress is provided where permissible under the National Building Code of Canada or other codes. | ● |  | n/a
E4.07 | Smoke detectors are connected to the fire alarm system. | ● | ♦ | n/a
Mechanical
M4.01 | Climate conditions eliminate all major risks to most of the collection. | ● | ♦ | n/a
M4.02 | The institution maintains at least ASHRAE B for cultural property Class 7. |  | ▲ | n/a
M4.03 | Final stage air filtration is a minimum MERV 12. | ● | ▲ | n/a
M4.04 | Facilities located in areas with higher pollutant concentrations have corresponding filtration. | ● | ▲ | n/a
M4.05 | Temperature and RH sensors are located in all spaces, not only in the return air ducts. | ● |  | n/a
M4.06 | Temperature and RH sensors are not located near windows, open doors, in front of vents, on exterior walls or in full sun. | ● |  | n/a
M4.07 | Climate readings can be taken at frequent (for example, 20-minute) intervals, and data can be downloaded and archived for later interpretation. | ● | ▲ | n/a
M4.08 | Each space has independent controls, which can be adjusted based on occupancy loads or lender requirements. | ● |  | n/a
M4.09 | There is automatic fire suppression. | ● | ▲ | n/a
Structural
S4.01 | Collections are protected against seismic shock in high-risk seismic zones. | ● | ♦ | n/a
5. Loading dock
Architectural
A5.01 | The loading dock is designed for access by the largest trucks used by the institution. | ● | ▲ | ▲
A5.02 | The loading dock is fully enclosed and can fit the largest trucks used by the institution. | ● | ▲ | ▲
A5.03 | The dock is sheltered if the loading dock is not fully enclosed. | ● | ▲ | ▲
A5.04 | There is a dock leveller or scissor lift. | ● | ▲ | ▲
A5.05 | Exterior doors have high-performance, pest-proof seals. | ●
A5.06 | There are no garbage bins or dumpsters inside the loading dock. | ● | ▲ | ▲
Electrical
E5.01 | Devices that can detect movement (for security purposes) are installed in receiving areas. | ● | ♦ | ♦
E5.02 | CCTV cameras are installed. | ● | ▲ | ♦
E5.03 | There are door contact sensors on exterior and garage doors. |  | ▲ | ▲
E5.04 | Smoke or heat detectors are connected to the fire alarm system. | ● | ♦ | ♦
Mechanical
M5.01 | The interior space is heated in winter. | ●