## Changelog (hidden)
Review Date | 2018-02-22
ORTECH Reference # | 91857
Reviewer | Ka-Ming Lin
Original workbook | Cooling Tower PM_e
NPRI Schedule 1 source document | 2016 and 2017 NPRI Substance List
Changes made
Issue: Workbook is protected, but not worksheets
Update: reference for Drift Factors no longer available (Tab Sheet 1 Cells E21:22), ASHRAE Standard is cited instead.

## Sheet1
Induced Draft Cooling Tower PM Emissions
The purpose of this spreadsheet is to determine the annual TPM emissions, as well as the PM10
and PM2.5 fractions of TPM from the pertinent drift data tables (see Tables 1, 2, and 3 below).
Instructions: Enter in the yellow cells the appropriate number. Results are shown in blue cells in the
three drift data tables below for the PM10 and PM2.5 fractions, and in red cells in row 16 for the TPM emissions.
Use one of the tables below that is the most representative of your cooling tower drift rate for the resulted
percentage values of PM10 and PM2.5 in TPM. Multiply these percentages by the TPM value in row 16
for the respective calculations of PM10 and PM2.5 emissions (see the calculation example in the guide).
| Circulating | Emission Rate | Annual Operating | Emission
Substance | Water (m3/hr) | (g/hr) | Period (hr) | Quantity | Unit
TPM |  | 0 |  | 0 | tonnes
Drift (expressed as a % of water flow), W [%]: |  |  | *** This value must be entered as a percentage // The Cell is formated as percentage
|  |  | 0.02% | AP-42, > 20 year old towers
|  |  | 0.005% | worst case new tower (source: ASHRAE Standard 189.1)
|  |  | 0.0025% | typical new tower (50% of ASHRAE Standard 189.1)
TDS, ppmw: |  |  | 33000 | sea water
|  |  | 12000 | AP-42, high dissolved solids
|  |  | 3000 | Great Lakes water * concentration factor ~10
DS Sp. Gr. : |  | 2.2 |  | Specific gravity of NaCl
Table 1 - Drift Data From Old Wood Herringbone Mist Eliminators (W = 0.01%)
CTI 0.01% drift data |  |  |  | Particulate emissions
Droplet | Fraction | Calculated residue | TPM | PM-10 | PM2.5
Ø (μm) | % smaller | Ø (μm) | mg/m3H2O | mg/m3H2O | mg/m3H2O
15 | 0.15 | 0 | 0
25 | 0.29 | 0 | 0
35 | 0.99 | 0 | 0
45 | 2.22 | 0 | 0
55 | 3.79 | 0 | 0
65 | 5.54 | 0 | 0
80 | 9.25 | 0 | 0
100 | 13.52 | 0 | 0
120 | 18.15 | 0 | 0
140 | 22.97 | 0 | 0
165 | 32.07 | 0 | 0
195 | 42.56 | 0 | 0
225 | 53.43 | 0 | 0
255 | 63.24 | 0 | 0
285 | 71.38 | 0 | 0
325 | 80.88 | 0 | 0
375 | 87.36 | 0 | 0
425 | 90.89 | 0 | 0
475 | 94.04 | 0 | 0
550 | 97.54 | 0 | 0
650 | 99.52 | 0 | 0
750 | 99.52 | 0 | 0
850 | 99.52 | 0 | 0
950 | 100 | 0 | 0
mg/m3H2O |  |  | 0 | 0 | 0
% TPM |  |  | #DIV/0! | #DIV/0! | #DIV/0!
source: J. Missimer, D. Wheeler, and K. Hennon, The relationship between SP
and HGBIK Drift Measurement Results, CTI paper TP98-16, 1998
Table 2 - Interpolated Drift Data for the Intermediate Drift Eliminators (W = 0.005%)
Representing the Averages of Table 1 and Table 3
Interpolated data, 0.005% water flow |  |  |  | Particulate emissions
Droplet | Fraction | Calculated residue | TPM | PM-10 | PM2.5
Ø (μm) | % smaller | Ø (μm) | mg/m3H2O | mg/m3H2O | mg/m3H2O
12.5 | 0.075 | 0 | 0
22.5 | 0.243 | 0 | 0
32.5 | 0.608 | 0 | 0
42.5 | 1.367 | 0 | 0
52.5 | 2.803 | 0 | 0
62.5 | 5.621 | 0 | 0
75 | 15.299 | 0 | 0
95 | 31.666 | 0 | 0
115 | 44.3295 | 0 | 0
135 | 52.4965 | 0 | 0
157.5 | 60.041 | 0 | 0
187.5 | 66.796 | 0 | 0
217.5 | 72.949 | 0 | 0
247.5 | 78.6655 | 0 | 0
277.5 | 83.0345 | 0 | 0
312.5 | 88.584 | 0 | 0
362.5 | 92.1855 | 0 | 0
412.5 | 94.615 | 0 | 0
462.5 | 96.5555 | 0 | 0
525 | 98.3055 | 0 | 0
625 | 99.76 | 0 | 0
mg/m3H2O |  |  | 0 | 0 | 0
% TPM |  |  | #DIV/0! | #DIV/0! | #DIV/0!
Table 3 - Drift Data From New Cellular Drift Eliminators (W = 0.0003%)
EPRI 0.0003% drift data |  |  | Particulate emissions
Droplet | Fraction | Calculated residue | TPM | PM-10 | PM2.5
Ø (μm) | % smaller | Ø (μm) | mg/m3H2O | mg/m3H2O | mg/m3H2O
10 | 0 | 0 | 0
20 | 0.196 | 0 | 0
30 | 0.226 | 0 | 0
40 | 0.514 | 0 | 0
50 | 1.816 | 0 | 0
60 | 5.702 | 0 | 0
70 | 21.348 | 0 | 0
90 | 49.812 | 0 | 0
110 | 70.509 | 0 | 0
130 | 82.023 | 0 | 0
150 | 88.012 | 0 | 0
180 | 91.032 | 0 | 0
210 | 92.468 | 0 | 0
240 | 94.091 | 0 | 0
270 | 94.689 | 0 | 0
300 | 96.288 | 0 | 0
350 | 97.011 | 0 | 0
400 | 98.34 | 0 | 0
450 | 99.071 | 0 | 0
500 | 99.071 | 0 | 0
600 | 100 | 0 | 0
mg/m3H2O |  |  | 0 | 0 | 0
% TPM |  |  | #DIV/0! | #DIV/0! | #DIV/0!
source: J. Reisman and G. Frisbie, Calculating Realistic PM10 Emissions from Cooling Towers
AWMA, Proceedings Florida Conference 2001, Session No. AM-1b